## README
M2 PV Performance — Workbook Excel
Reverse engineering dari pv_pipeline/ (notebook 20260514stringmap_v1.5.ipynb)
Iterasi log
Iterasi | Tanggal | Detector | Sheet yang ditambah
1 (Phase 1) | 2026-05-28 | — | Hanya dokumen overview (.docx + .md). Belum ada Excel.
2 | 2026-05-28 | M2eAvailability | README, Config, Raw_Data, EmptyPVMap, Helpers_M2e, M2e_Availability, M2e_AllStrings, Findings_Summary
3 | 2026-05-28 | M2bPeerZScore | Meteo_Dummy, PanelSpec, Raw_Data_M2b, Helpers_M2b, M2b_PeerZScore, M2b_StringStatus, Hampel_Preprocessing, M2b_StatComparison
Cara membaca
• Sheet 'Config' adalah single source of truth untuk semua threshold. Edit di sini → seluruh workbook recalc.
• Sheet 'Raw_Data' berisi data dummy realistis. Ganti dengan data aktual mu (paste over) untuk pakai workbook ini di lapangan.
• Sheet 'Helpers_M2e' adalah JEMBATAN antara Raw_Data dan M2e_Availability. Tiap kolom punya formula yang ekuivalen dengan satu langkah di pv_pipeline/availability.py.
• Sheet 'M2e_Availability' menampilkan hasil akhir per inverter & per string + severity. Sheet 'M2e_AllStrings' mereplika output sheet xlsx Python.
• Severity dihitung via IFS() dari uptime_pct ke threshold di Config.
• Workbook ini akan TUMBUH per iterasi — sheet baru ditambah tanpa mengubah yang lama.

## Config
M2 Configuration (mirror config/m2_config.yaml)
Section | Key | Value | Unit / Notes
m2e.severity | critical_below | 90 | % uptime; < ini → CRITICAL
m2e.severity | high_below | 95 | % uptime; < ini → HIGH
m2e.severity | medium_below | 97 | % uptime; < ini → MEDIUM
m2e.severity | info_below | 99 | % uptime; < ini → INFO; ≥ ini → NORMAL
m2e.severity | emit_normal | 0 | 1=emit NORMAL findings, 0=skip
m2e.string_proxy | pstr_zero_threshold_kw | 0.1 | kW; PV power < ini → string dianggap mati
m2e.string_proxy | sibling_median_active_kw | 1 | kW; median sibling >= ini → timestamp 'produktif'
m2e.string_proxy | min_active_siblings_pct | 50 | %; minimum % sibling aktif → 'qualified' timestamp
m2e.string_proxy | debounce_consecutive_steps | 2 | step; run candidate >= ini → genuine event. DUMMY=2 (original spec). PRODUKSI IKN=20 (~1h40m persist).
system | interval_minutes | 5 | menit; median selisih Start Time (auto-detected, override saat dummy)
system | pv_max | 28 | PV string per inverter (hardcoded Huawei cap)
system | n_pv_total_in_workbook | 5 | PV string yang ada di sheet ini (PV1..PV5)
m2b | poa_threshold_wm2 | 300 | W/m²; ¦z¦ Z-score hanya hitung saat POA > ini (spec 4.2.1)
m2b | poa_floor_wm2 | 50 | W/m²; sunset fix — POA harus > ini (sensor lag protection)
m2b | z_threshold | 2.5 | ¦z¦ > ini → flag suspect (spec 4.2.1)
m2b | z_high_threshold | 3.5 | ¦z¦ > ini → severity HIGH; else MEDIUM
m2b | voc_ratio_threshold | 0.95 | voc_actual/voc_string_nominal > ini → confirm high_R (spec 4.2.3)
m2b | stat_method | median | mean ¦ median ¦ both (z_primary picker)
m2b | min_peer_strings | 3 | min sibling per inverter untuk valid peer comparison
m2b | min_daylight_samples | 10 | min samples lulus POA gate per inverter
m2b | i_clip_floor_a | 0.1 | clip(lower=0.1A) untuk hindari divide-by-zero saat R=V/I
voc_estimator | i_threshold_a | 0.5 | I < ini → dianggap open-circuit (sunrise/sunset)
voc_estimator | min_voc_v | 10 | V > ini → buang zero-reading sample
voc_estimator | min_samples | 3 | minimum samples valid untuk median voc
preprocessing | hampel_window | 15 | samples; rolling window (75 menit @ 5-min)
preprocessing | hampel_max_deviation | 3 | MAD-sigma; ¦x - median¦ / MAD > ini → outlier
preprocessing | enabled | 0 | 1=apply Hampel cleaning, 0=skip (raw V/I)
poa | default_source | pyranometer_avg | single source di dummy (production: 5 sources)

## Raw_Data
Raw_Data (dummy realistis — 2 inverter × 12 timestep)
Skenario: INV01 punya PV3 fault 6-timestep; INV02 down 4-timestep. PV5 (kedua inverter) ada di EmptyPVMap.
Inverter_ID | Start Time | Inverter status | PV1 Power(kW) | PV2 Power(kW) | PV3 Power(kW) | PV4 Power(kW) | PV5 Power(kW)
WB02-INV01 | 2026-05-14 10:00 | Grid connected | 5 | 4.9 | 5.1 | 5 | 0
WB02-INV01 | 2026-05-14 10:05 | Grid connected | 5.05 | 4.94 | 5.1 | 5.03 | 0
WB02-INV01 | 2026-05-14 10:10 | Grid connected | 5.1 | 4.98 | 5.1 | 5.06 | 0
WB02-INV01 | 2026-05-14 10:15 | Grid connected | 5.15 | 5.02 | 0 | 5 | 0
WB02-INV01 | 2026-05-14 10:20 | Grid connected | 5 | 5.06 | 0 | 5.03 | 0
WB02-INV01 | 2026-05-14 10:25 | Grid connected | 5.05 | 4.9 | 0 | 5.06 | 0
WB02-INV01 | 2026-05-14 10:30 | Grid connected | 5.1 | 4.94 | 0 | 5 | 0
WB02-INV01 | 2026-05-14 10:35 | Grid connected | 5.15 | 4.98 | 0 | 5.03 | 0
WB02-INV01 | 2026-05-14 10:40 | Grid connected | 5 | 5.02 | 0 | 5.06 | 0
WB02-INV01 | 2026-05-14 10:45 | Grid connected | 5.05 | 5.06 | 5.1 | 5 | 0
WB02-INV01 | 2026-05-14 10:50 | Grid connected | 5.1 | 4.9 | 5.1 | 5.03 | 0
WB02-INV01 | 2026-05-14 10:55 | Grid connected | 5.15 | 4.94 | 5.1 | 5.06 | 0
WB02-INV02 | 2026-05-14 10:00 | Grid connected | 5 | 5 | 5 | 5 | 0
WB02-INV02 | 2026-05-14 10:05 | Grid connected | 5 | 5 | 5 | 5 | 0
WB02-INV02 | 2026-05-14 10:10 | Grid connected | 5 | 5 | 5 | 5 | 0
WB02-INV02 | 2026-05-14 10:15 | Grid connected | 5 | 5 | 5 | 5 | 0
WB02-INV02 | 2026-05-14 10:20 | Shutdown command | 0 | 0 | 0 | 0 | 0
WB02-INV02 | 2026-05-14 10:25 | Shutdown command | 0 | 0 | 0 | 0 | 0
WB02-INV02 | 2026-05-14 10:30 | Shutdown command | 0 | 0 | 0 | 0 | 0
WB02-INV02 | 2026-05-14 10:35 | Shutdown command | 0 | 0 | 0 | 0 | 0
WB02-INV02 | 2026-05-14 10:40 | Grid connected | 5 | 5 | 5 | 5 | 0
WB02-INV02 | 2026-05-14 10:45 | Grid connected | 5 | 5 | 5 | 5 | 0
WB02-INV02 | 2026-05-14 10:50 | Grid connected | 5 | 5 | 5 | 5 | 0
WB02-INV02 | 2026-05-14 10:55 | Grid connected | 5 | 5 | 5 | 5 | 0

## EmptyPVMap
EmptyPVMap — slot PV yang fisik tidak terpasang (skip dari peer comparison)
Replica config/strings.yaml (245 inverter dalam file aktual). Di sini hanya entry yang relevan untuk dummy.
Inverter_ID | Empty PV indices (CSV) | Note
WB02-INV01 | 5 | DEMO: PV5 EMPTY by design
WB02-INV02 | 5 | DEMO: PV5 EMPTY by design
WB01-INV01 | 19,20,21,22,23,24,25,26,27,28 | Pola WB01 produksi (PV19-28 kosong)
WB03-INV01 |  | (contoh: tidak ada slot kosong)
WB05-INV05 | 5 | DEMO M2b: PV5 EMPTY

## Helpers_M2e
Helpers_M2e — derived columns dari Raw_Data (per-row formulas)
Setiap kolom = 1 langkah di pv_pipeline/availability.py. Edit Raw_Data → recalc otomatis.
Inverter_ID | Start Time | status_raw | _status_class | sib_median_kW | active_count | active_pct | qualified | is_on | cand_PV1 | run_id_PV1 | run_len_PV1 | in_event_PV1 | cand_PV2 | run_id_PV2 | run_len_PV2 | in_event_PV2 | cand_PV3 | run_id_PV3 | run_len_PV3 | in_event_PV3 | cand_PV4 | run_id_PV4 | run_len_PV4 | in_event_PV4 | cand_PV5 | run_id_PV5 | run_len_PV5 | in_event_PV5

## M2e_Availability
M2e Availability — output finding per inverter & per string
Section A: per-inverter uptime%. Section B: per-string proxy down. Severity di-derive dari uptime_pct vs threshold di Config.
A. Per-inverter daily uptime
Inverter_ID | n_on | n_down | denom | uptime_pct | downtime_min | severity | threshold_breached | message
WB02-INV01
WB02-INV02
B. Per-string proxy down (event_minutes_total + uptime_pct + severity)
Inverter_ID | PV_string | daylight_minutes_inv | event_minutes | n_events | string_uptime_pct | severity | is_empty | message
WB02-INV01 | PV1
WB02-INV01 | PV2
WB02-INV01 | PV3
WB02-INV01 | PV4
WB02-INV01 | PV5
WB02-INV02 | PV1
WB02-INV02 | PV2
WB02-INV02 | PV3
WB02-INV02 | PV4
WB02-INV02 | PV5

## M2e_AllStrings
M2e_AllStrings — tabel rapi per (inverter × PV string) — replika output Python
Setiap baris = 1 PV slot. status ∈ {EMPTY, NO_DAYLIGHT, NORMAL, INFO, MEDIUM, HIGH, CRITICAL}. Pull dari M2e_Availability Section B.
inverter_id | pv_string | status | uptime_pct | downtime_minutes | event_minutes | n_events | daylight_minutes

## Findings_Summary
Findings_Summary — agregat semua finding NON-NORMAL & NON-EMPTY
Saat ini hanya M2e. Akan tumbuh: M2b, M2a, IsolationForest, dst. Setiap iterasi tambah sheet detector → tambah baris di sini.
Source Sheet | sub_module | inverter_id | pv_string | severity | value (uptime_pct) | threshold | message
M2e_Availability!A (inverter) | M2e_inverter
M2e_Availability!A (inverter) | M2e_inverter
M2e_Availability!B (string proxy) | M2e_string_proxy |  |  |  |  | (see Config)
M2e_Availability!B (string proxy) | M2e_string_proxy |  |  |  |  | (see Config)
M2e_Availability!B (string proxy) | M2e_string_proxy |  |  |  |  | (see Config)
M2e_Availability!B (string proxy) | M2e_string_proxy |  |  |  |  | (see Config)
M2e_Availability!B (string proxy) | M2e_string_proxy |  |  |  |  | (see Config)
M2e_Availability!B (string proxy) | M2e_string_proxy |  |  |  |  | (see Config)
M2e_Availability!B (string proxy) | M2e_string_proxy |  |  |  |  | (see Config)
M2e_Availability!B (string proxy) | M2e_string_proxy |  |  |  |  | (see Config)
M2e_Availability!B (string proxy) | M2e_string_proxy |  |  |  |  | (see Config)
M2e_Availability!B (string proxy) | M2e_string_proxy |  |  |  |  | (see Config)
--- M2b PeerZScore ---
M2b_PeerZScore!C | M2b_peer_zscore | WB05-INV05 | PV1
M2b_PeerZScore!C | M2b_peer_zscore | WB05-INV05 | PV2
M2b_PeerZScore!C | M2b_peer_zscore | WB05-INV05 | PV3
M2b_PeerZScore!C | M2b_peer_zscore | WB05-INV05 | PV4
M2b_PeerZScore!C | M2b_peer_zscore | WB05-INV05 | PV5 | EMPTY | - | - | -

## PanelSpec
PanelSpec — Jinko JKM625N 78HL4-BDV (mirror config/panel_spec.yaml)
Konsumen: PanelSpec.voc_at_cell_temp + voc_string_nominal di peer_zscore.py
Parameter | Value | Unit | Notes
panel_model | Jinko JKM625N 78HL4-BDV |  | Bifacial Tiger Neo dual-glass
voc_stc_v | 55.72 | V | Open-circuit voltage @ STC (1000 W/m², 25°C cell)
vmp_stc_v | 46.1 | V | Max-power voltage @ STC
imp_stc_a | 13.56 | A | Max-power current @ STC
isc_stc_a | 14.27 | A | Short-circuit current @ STC
pmax_stc_w | 625 | W | Max power @ STC
voc_noct_v | 52.93 | V | Voc @ NOCT (800 W/m², 20°C ambient)
temp_coef_voc_pct_per_c | -0.25 | %/°C | Voc decreases when Tcell rises
temp_coef_pmax_pct_per_c | -0.29 | %/°C | Pmax temperature coefficient
temp_coef_isc_pct_per_c | 0.045 | %/°C | Isc temperature coefficient (small +)
t_stc_c | 25 | °C | STC reference temperature
max_system_voltage_v | 1500 | V | IEC limit
default_modules_per_string | 26 | modules | Fallback (WB03-10)
modules_per_string_WB01 | 24 | modules | PLTS-IKN WB01 layout
modules_per_string_WB02 | 24 | modules | PLTS-IKN WB02 layout
modules_per_string_WB03_10 | 26 | modules | PLTS-IKN WB03-10 layout
voc_at_cell_temp(T_cell) — Excel formula
Input: cell_temp_c → | 30 | °C (edit untuk recalc)
voc_per_module = voc_stc × (1 + temp_coef_voc/100 × (T - 25)) |  | V per modul
voc_string_WB01_WB02 (24 modules) |  | V per string (cold Voc skenario)
voc_string_WB03_WB10 (26 modules) |  | V per string

## Raw_Data_M2b
Raw_Data_M2b — extended dummy data (WB05-INV05, 24 timestep)
Skenario: 06:00-06:55 sunrise (I≈0, V≈Voc), 12:00-13:55 noon (full sun). PV3 punya HIGH-R fault (I drop 60%, V naik sedikit) → expected flag.
Inverter_ID | Start Time | Inverter status | PV1 input voltage(V) | PV1 input current(A) | PV2 input voltage(V) | PV2 input current(A) | PV3 input voltage(V) | PV3 input current(A) | PV4 input voltage(V) | PV4 input current(A) | PV5 input voltage(V) | PV5 input current(A)
WB05-INV05 | 2026-05-14 06:00 | Grid connected | 1467.49 | -0.023 | 1469.34 | 0.023 | 1469.96 | -0.036 | 1468.08 | -0.042 | 0 | 0
WB05-INV05 | 2026-05-14 06:05 | Grid connected | 1462.29 | 0.071 | 1464.79 | 0.106 | 1463.07 | 0.11 | 1465.42 | 0.052 | 0 | 0
WB05-INV05 | 2026-05-14 06:10 | Grid connected | 1469.42 | 0.105 | 1471.89 | 0.123 | 1468.43 | 0.099 | 1471.45 | 0.15 | 0 | 0
WB05-INV05 | 2026-05-14 06:15 | Grid connected | 1470.22 | 0.193 | 1469.59 | 0.151 | 1471.39 | 0.158 | 1471.52 | 0.154 | 0 | 0
WB05-INV05 | 2026-05-14 06:20 | Grid connected | 1467.96 | -0.012 | 1467.36 | -0.018 | 1467.45 | -0.013 | 1469.59 | -0.004 | 0 | 0
WB05-INV05 | 2026-05-14 06:25 | Grid connected | 1464.77 | 0.086 | 1466.29 | 0.053 | 1464.39 | 0.065 | 1464.36 | 0.03 | 0 | 0
WB05-INV05 | 2026-05-14 06:30 | Grid connected | 1472.12 | 0.146 | 1473.27 | 0.156 | 1470.81 | 0.081 | 1471.16 | 0.105 | 0 | 0
WB05-INV05 | 2026-05-14 06:35 | Grid connected | 1465.62 | 0.17 | 1464.73 | 0.178 | 1465.77 | 0.184 | 1463.17 | 0.163 | 0 | 0
WB05-INV05 | 2026-05-14 06:40 | Grid connected | 1467.95 | 0.092 | 1467.21 | 0.024 | 1469.6 | 0.054 | 1465.98 | 0.007 | 0 | 0
WB05-INV05 | 2026-05-14 06:45 | Grid connected | 1464.26 | 0.118 | 1461.35 | 0.114 | 1465.08 | 0.128 | 1464.98 | 0.162 | 0 | 0
WB05-INV05 | 2026-05-14 06:50 | Grid connected | 1462.84 | 0.148 | 1461.18 | 0.158 | 1460.56 | 0.138 | 1461.93 | 0.19 | 0 | 0
WB05-INV05 | 2026-05-14 06:55 | Grid connected | 1470.76 | 0.021 | 1472.41 | 0.09 | 1469.95 | 0.067 | 1471.19 | 0.018 | 0 | 0
WB05-INV05 | 2026-05-14 12:00 | Grid connected | 1205.31 | 13.015 | 1202.2 | 12.994 | 1238.4 | 5.248 | 1205.72 | 13.045 | 0 | 0
WB05-INV05 | 2026-05-14 12:05 | Grid connected | 1198.43 | 12.912 | 1195.26 | 12.866 | 1231.1 | 5.173 | 1197.98 | 12.83 | 0 | 0
WB05-INV05 | 2026-05-14 12:10 | Grid connected | 1198.66 | 13.052 | 1199.3 | 12.986 | 1235.75 | 5.229 | 1198.41 | 12.996 | 0 | 0
WB05-INV05 | 2026-05-14 12:15 | Grid connected | 1207.67 | 13.047 | 1206.41 | 13.017 | 1243.51 | 5.227 | 1206.84 | 13.017 | 0 | 0
WB05-INV05 | 2026-05-14 12:20 | Grid connected | 1192.05 | 13.08 | 1194.57 | 12.996 | 1227.88 | 5.233 | 1191.99 | 13.003 | 0 | 0
WB05-INV05 | 2026-05-14 12:25 | Grid connected | 1206.86 | 13.05 | 1208.2 | 12.99 | 1241.56 | 5.202 | 1206.66 | 13.018 | 0 | 0
WB05-INV05 | 2026-05-14 12:30 | Grid connected | 1205.6 | 13.012 | 1203.28 | 13.036 | 1241.22 | 5.196 | 1202.43 | 13.047 | 0 | 0
WB05-INV05 | 2026-05-14 12:35 | Grid connected | 1197.75 | 12.976 | 1198.52 | 12.97 | 1234.91 | 5.128 | 1200.75 | 12.967 | 0 | 0
WB05-INV05 | 2026-05-14 12:40 | Grid connected | 1208.9 | 13.095 | 1207.45 | 13.099 | 1243.33 | 5.207 | 1207.02 | 13.176 | 0 | 0
WB05-INV05 | 2026-05-14 12:45 | Grid connected | 1196.06 | 13.078 | 1198.07 | 13.135 | 1232.35 | 5.256 | 1194.86 | 13.065 | 0 | 0
WB05-INV05 | 2026-05-14 12:50 | Grid connected | 1207.67 | 13.049 | 1205.73 | 13.032 | 1243.74 | 5.245 | 1206.13 | 13.07 | 0 | 0
WB05-INV05 | 2026-05-14 12:55 | Grid connected | 1193.66 | 12.923 | 1192.22 | 12.868 | 1230.64 | 5.137 | 1193.66 | 12.918 | 0 | 0

## Meteo_Dummy
Meteo_Dummy — POA (Plane-of-Array) per timestamp
Single source 'pyranometer_avg' (dummy). Produksi: 5 source fan-out (pyranometer_per_ws, pyranometer_avg, pvlib_clearsky_ineichen/simplified_solis/haurwitz).
Start Time | POA pyranometer_avg (W/m²) | Notes
2026-05-14 06:00 | 30 | sunrise (below gate)
2026-05-14 06:05 | 34.5 | sunrise (below gate)
2026-05-14 06:10 | 39.1 | sunrise (below gate)
2026-05-14 06:15 | 43.6 | sunrise (below gate)
2026-05-14 06:20 | 48.2 | sunrise (below gate)
2026-05-14 06:25 | 52.7 | sunrise (below gate)
2026-05-14 06:30 | 57.3 | sunrise (below gate)
2026-05-14 06:35 | 61.8 | sunrise (below gate)
2026-05-14 06:40 | 66.4 | sunrise (below gate)
2026-05-14 06:45 | 70.9 | sunrise (below gate)
2026-05-14 06:50 | 75.5 | sunrise (below gate)
2026-05-14 06:55 | 80 | sunrise (below gate)
2026-05-14 12:00 | 847.6 | noon (above gate)
2026-05-14 12:05 | 857.5 | noon (above gate)
2026-05-14 12:10 | 860.7 | noon (above gate)
2026-05-14 12:15 | 878 | noon (above gate)
2026-05-14 12:20 | 861.1 | noon (above gate)
2026-05-14 12:25 | 881.5 | noon (above gate)
2026-05-14 12:30 | 872.2 | noon (above gate)
2026-05-14 12:35 | 881.9 | noon (above gate)
2026-05-14 12:40 | 895.2 | noon (above gate)
2026-05-14 12:45 | 889 | noon (above gate)
2026-05-14 12:50 | 894.5 | noon (above gate)
2026-05-14 12:55 | 912.6 | noon (above gate)

## Helpers_M2b
Helpers_M2b — derived columns per row dari Raw_Data_M2b
Per-row: POA value (VLOOKUP dari Meteo_Dummy), mask_poa, R_str per PV. Aggregate (R_str median per PV, fleet stats) ada di sheet M2b_PeerZScore.
Inverter_ID | Start Time | status | POA_Wm2 | mask_poa | is_on | PV1_V | PV1_I | PV1_R | PV1_voc_cand | PV2_V | PV2_I | PV2_R | PV2_voc_cand | PV3_V | PV3_I | PV3_R | PV3_voc_cand | PV4_V | PV4_I | PV4_R | PV4_voc_cand | PV5_V | PV5_I | PV5_R | PV5_voc_cand

## M2b_PeerZScore
M2b PeerZScore — agregat per PV (R_str median dari mask_poa samples) + Z-score + voc_ratio + fault decision
Spec 4.2.1: ¦z¦ > 2.5 → flag. Spec 4.2.3 high_R: AND voc_ratio > 0.95 → emit. Confidence = min(90, ¦z¦/4*100). Severity: ¦z¦ > 3.5 HIGH else MEDIUM.
A. Per-PV string metrics (WB05-INV05, 5 PV strings)
PV_string | R_str (median) | voc_actual_v (median I<0.5A) | voc_string_nominal_v | voc_ratio | n_R_samples | n_voc_samples
PV1
PV2
PV3
PV4
PV5
B. Fleet statistics across PV1..PV5 (skip blanks)
Metric | Value
R_str fleet mean
R_str fleet median
R_str fleet std (sample stdev)
C. Z-score & fault decision per PV
PV_string | z_mean | z_median | z_primary (per stat_method) | flagged_by_z (¦z¦>2.5) | voc_ok (voc_ratio>0.95) | emit_finding | fault_type | severity | confidence_pct | message
PV1
PV2
PV3
PV4
PV5

## M2b_StringStatus
M2b_StringStatus — replika Python self.artifacts['StringStatus']
Pull dari M2b_PeerZScore sections A & C.
poa_source | inverter_id | wb_id | pv_string | status | rstr | rstr_fleet_median | rstr_fleet_std | z_mean | z_median | voc_actual_v | voc_string_nominal_v | voc_ratio | voc_ok | emitted_finding
pyranometer_avg | WB05-INV05 | WB05 | PV1
pyranometer_avg | WB05-INV05 | WB05 | PV2
pyranometer_avg | WB05-INV05 | WB05 | PV3
pyranometer_avg | WB05-INV05 | WB05 | PV4
pyranometer_avg | WB05-INV05 | WB05 | PV5 | EMPTY

## M2b_StatComparison
M2b StatComparison — Z-score mean vs median cross-check
Spec dual-stat: ¦z_mean¦ dan ¦z_median¦ dievaluasi. flagged_by_mean / flagged_by_median. Median lebih robust ke outlier (PV3 fault tidak skew median sebanyak mean).
PV_string | R_str | z_mean (vs fleet_mean) | z_median (vs fleet_median) | ¦z_mean¦ > 2.5? | ¦z_median¦ > 2.5? | agree (both flagged)? | diff ¦z_mean - z_median¦
PV1
PV2
PV3
PV4
PV5

## Hampel_Preprocessing
Hampel Preprocessing — A/B comparison V series original vs Hampel-cleaned
Demo Wave 9: rolling median window 15 (75-min) + MAD-based outlier mask. Approximation of pvanalytics.quality.outliers.hampel(). Toggle via cfg_enabled.
Note: window 15 butuh ≥15 samples. Dummy 24 timestep cukup untuk demo.
Start Time | PV3_V_original | rolling_median (window 15) | abs_dev_from_median | rolling_MAD | deviation_in_MAD_sigma | is_outlier | PV3_V_cleaned